THE INTERNATIONAL JOURNAL OF

SCIENCE & TECHNOLEDGE

To Study The Effect Of Seismic And Wind Loads On Hyperbolic Cooling Tower Of Varying Dimension And RCC Shell Thickness

1.Introduction

The natural draught cooling tower is a very important and essential component in the thermal and nuclear power stations. These are huge structures and also show thin shell structures. Cooling towers are subjected to its self-weight and the dynamic load such as an earthquake motion and a wind effects. In the absence of earthquake loading, wind constitutes the main loading for the design of natural draught cooling towers. A lot of research work was reported in the literature on the seismic &wind load on cooling tower [1 to 5].

G. Murali et al., [1] Response of cooling tower to wind load. He studied the two cooling towers of 122m and 200m high above ground level. They calculated the values like meridional forces and bending moments. D.Makovička, Acta Polytechnica [2], Studied Response Analysis of an RC Cooling Tower under Seismic and Windstorm Effects. The calculated values of the envelopes of the displacements and the internal forces due to seismic loading states are compared with the envelopes of the loading states due to the dead, operational and live loads, wind and temperature actions. Finite element model is established; then mechanical characters of the tower under gravity, temperature load and wind loads are analyzed. A. M. El Ansary [3], Optimum shape and design of cooling tower, study is To Develop a numerical tool that is capable Of Achieving An Optimum shape

And design of hyperbolic cooling towers based on coupling a non-linear finite element model developed in-house and a genetic algorithm optimization technique. R.L.Norton [4], studied the effect of asymmetric imperfection on the earth quake response of hyperbolic cooling tower. Shailesh S [5], studied the problem of natural draught hyperbolic cooling towers. The main interest is to demonstrate that the column supports to the tower could be replaced by equivalent shell elements so that the software developed could easily be utilized.

2.Description Of The Geometry Of The Tower

For the purposes of comparison, a real tower from one of the thermal power station is considered in the current study as the Reference Tower. The total height of the tower is 143.5 m. As shown in Figure. 1, the tower has a base, throat and top radii of 55m, 30.5m and 31.85m, respectively, with the throat located 107.75m above the base. It has a constant shell-wall thickness of 200mm and at top 500 mm. The tower is constructed of reinforced concrete having a, unit weight of concrete 24 Kn/m3, Poisson’s ratio of 0.15 and Young modulus of 31GPa. For the comparssion the existing CT dimensions and RCC shell thickness should be increased and decreased and all the details of the CT as shown in Table: 1.

The geometry of the Hyperboloid revolution:

In which Ro is the horizontal radius at any vertical coordinate, Y with the origin of coordinates being defined by the center of the tower throat, ao is the radius of the throat, and b is some characteristic dimension of the hyperboloid.

Figure 1: Geometry Of BTPS

| Sl.No. | Description | Parametric value |
| --- | --- | --- |
|  |  | CT1 (Ref. Shell) | CT2 (Decreased) | CT3 (Increased) |
| 1 | Total height, H | 143.5 m | 136.2 m | 150.67 m |
| 2 | Height of throat, Hthr | 107.75 m | 102.36 m | 113.13 m |
| 3 | Diameter at top, Dt | 63.6 m | 60.5 m | 66.8 m |
| 4 | Diameter at bottom, Db | 110 m | 104.5 m | 115.5 m |
| 5 | Diameter at throat level, Dthr | 61 m | 57.94 m | 64 m |
| 6 | Column Height | 9.2 m | 8.74 m | 9.66 m |
| 7 | Thickness of RCC shell | 200mm | 250mm | 150mm |

Table 1: Geometric Details Of Cooling Towers

Note: CT1: Bellary Thermal Power Plant As Reference Tower

CT2: Decreased The Dimensions And Increased The Thickness Of Shell

CT3: Increased The Thickness And Decreased The Thickness Of Shell

3.Forces Consider For Analysis

3.1. Earthquake Loads

The seismic analysis is carried out in accordance with IS: 1893 by modal analysis of the hyperbolic cooling towers, the earthquake analysis of the shell is carried out by response spectrum method. Earthquake analysis for the fill supporting structures (RCC frames) is carried out by response spectrum method. For the calculation of the design spectrum, the following factors were considered as per IS 1893 (part I) 2002.

Zone factor:   For Zone III				= 0.16

Importance factor (I)				= 1.00

Response reduction factor (R) 	                     = 3.00

Average response acceleration coefficient Sa/g =Soft soil site condition

The design horizontal seismic coefficient Ah for 0.5g, 0.6g & 0.7g of a structure shall be determined by the following expression: Maximum   considered   Earthquake   (MCE)   of   2% probability.

Figure 2: Response Spectra For 0.5g                Figure 3: Response Spectra For 0.6g

Figure 4: Response Spectra For 0.7g

3.2.Wind Load

The wind pressure at a given height [Pz)] will be computed as per the stipulations of IS: 875 (part 3)-1987. For computing the design wind pressure at a given height the basic wind speed (Vb) will be taken as Vb=39 m/s at 9.2m height above mean ground level. For computing design wind speed (Vz) at a height z, the risk coefficient K1=1.06 will be considered. For coefficient K2 terrain category 2 as per table 2 of IS: 875 (part-3)-1987 will be considered. The wind direction for design purpose will be the one which world induces worst load condition. Coefficient K3 will be 1 for the tower under consideration. The wind pressure at a given height wills b e computed theoretically in accordance to the IS codal provision given as under:

Pz = 0.6 Vz2 N/m2   …………………… (4.1)

Where Vz =Vb x K1 x K2 x K3………. (4.2)

Computation of wind pressure (Pz) along the wind direction by Gust factor method

4.Finite Element Analysis

Due to the complexity of the material properties, the boundary conditions and the tower structure, finite element analysis is adopted. The finite element analysis of the cooling towers has been carried out using ANSYS V.10. The shell element is the most efficient element for the solution of shells having the arbitrary geometry and it accounts for both membrane and bending actions. The analysis has been carried out using 8-noded shell element (SHELL 93) with 5 degrees of freedom per node. In the present study, only shell portion of the cooling towers has been modeled and fixity has been assumed at the base.

4.1.Material Properties For Analysis Of CT

- Young modulus: 31Gpa

- Poisson Ratio: 0.15

- Density of RCC: 25 Kn/m3

5.Tabulations & Results

- CT 1: Existing thermal power plant tower as reference tower.

- CT 2: Decrease the Dimensions of cooling tower & Increase the thickness.

- CT 3: Increase the Dimension of cooling tower & Decrease the thickness.

5.1.Static Analysis

Static analysis is carried only for self weight. The Geometry of the model is created in ANSYS by using key points. By assigning the loads and boundary conditions to the model and selecting static analysis the problem was solved. The results were compiled in general post processor

Figure 5: Key Points                       Figure 6: Geometric Model With Bc         Figure 7: Thickness Of Rcc Shell

Figure 8: Deflection In CT1              Figure 9: Principal Stress In CT1            Figure 10: Principal Strain In CT1

Figure 11: Von Mises Stress In CT1            Figure 12: Von Mises Strain In CT1

| Series | Max. Deflection (mm) | Max. Principle | Max. Von Mises |
| --- | --- | --- | --- |
|  |  | Stress (MPa) | Strain | Stress (MPa) | Strain |
| CT 1 | 6.828 | 0.049038 | 0.162 x10-4 | 2.716 | 0.859x10-4 |
| CT 2 | 6.079 | 0.054505 | 0.146 x10-4 | 2.521 | 0.796x10-4 |
| CT 3 | 7.032 | 0.063277 | 0.157x10-4 | 2.651 | 0.838 x10-4 |

Table 2: Results Of Static Analysis

5.2.Modal Analysis

This method is used to calculate natural frequency and mode shapes. The Geometry of the model was created in ANSYS by using key points. By assigning the loads and boundary conditions to the model and selecting Modal analysis, giving number of modes to extract as 50 frequencies and solved the problem. The results were compiled in general post processor.

Figure 13:  Deflection At 1st Mode @ Freq 1.022   In CT1

&

Figure 14:  Principal Stress At 1st Mode @ Freq 1.022  In CT1

Figure15:  Principal Strain At 1st Mode          Figure 16:  Von Mises Stress                Figure 17:  Von Mises At 1st @ Freq

Freq  1.022 In CT 1                         1st Mode @ Freq 1.022 In CT 1            1st Mode @ Freq 1.022 In CT 1

| Series | Modes | Freq (HZ) | Max. Deflection (mm) | Max. Principal | Max. Von Mises |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Stress (MPa) | Strain | Stress (MPa) | Strain |
| CT1 | 1 | 1.022 | 0.02515 | 0.002972 | 0.941 x10-7 | 0.00298 | 0.943 x10-7 |
|  | 5 | 1.305 | 0.024832 | 0.001647 | 0.521 x10-7 | 0.001652 | 0.523 x10-7 |
|  | 10 | 1.512 | 0.01977 | 0.001328 | 0.415 x10-7 | 0.001303 | 0.412 x10-7 |
| CT2 | 1 | 1.137 | 0.026128 | 0.001849 | 0.582 x10-7 | 0.001824 | 0.577 x10-7 |
|  | 5 | 1.49 | 0.020358 | 0.001381 | 0.434 x10-7 | 0.001355 | 0.429 x10-7 |
|  | 10 | 1.67 | 0.021157 | 0.002332 | 0.732 x10-7 | 0.002277 | 0.194 x10-8 |
| CT3 | 1 | 0.8076 | 0.026254 | 0.00146 | 0.446 x10-7 | 0.001394 | 0.441 x10-7 |
|  | 5 | 0.9904 | 0.025641 | 0.002206 | 0.665 x10-7 | 0.002014 | 0.637 x10-7 |
|  | 10 | 1.189 | 0.020245 | 0.002329 | 0.705 x10-7 | 0.00212 | 0.671 x10-7 |

Table 3: Results Of Modal Analysis

5.3.Response Spectra Analysis: 0.5G, 0.6G & 0.7G

Response spectrum analysis is carried out for 0.5g,0.6g & 0.7g The Geometry of the model in ANSYS by using key points & we have to input material models, shell element & make mesh to model in Pre processor. By assigning the loads& boundary conditions to the model and before doing Spectrum analysis first we to do Modal analysis, after we have to select the spectrum analysis & apply all input data’s such as frequencies, seismic co-efficient, square root sum of squares (SRSS) method and solve the problem in solution & read the results in General post processor.

Figure 18: Deflection At 0.5g, CT1                  Figure 19: Von Mises Stress                    Figure 20: Von Mises Strain

At 0.5g, CT1                                     At 0.5g, CT1

Figure 21: Principal Stress At 0.5g, CT1              Figure 22: Principal Strain At 0.5g, CT1

| Series | Max. Deflection (mm) | Max. Principle | Max. Von Mises |
| --- | --- | --- | --- |
|  |  | Stress (MPa) | Strain | Stress (MPa) | Strain |
| CT 1 | 6.523 | 0.613682 | 0.195 x10-4 | 0.609945 | 0.193 x10-4 |
| CT 2 | 5.902 | 0.578328 | 0.183 x10-4 | 0.589108 | 0.186 x10-4 |
| CT 3 | 0.119 x10-8 | 0.231 x10-9 | 0.705 x10-14 | 0.220 x10-9 | 0.695 x10-14 |

Table 4: Results Of Response Spectrum Analysis: 0.5g

| Series | Max. Deflection (mm) | Max. Principle | Max. Von Mises |
| --- | --- | --- | --- |
|  |  | Stress (MPa) | Strain | Stress (MPa) | Strain |
| CT 1 | 8.547 | 0.756147 | 0.244 x10-4 | 0.773432 | 0.245 x10-4 |
| CT 2 | 7.083 | 0.693995 | 0.220 x10-4 | 0.706931 | 0.224 x10-4 |
| CT 3 | 0.143 x10-8 | 0.277 x10-9 | 0.845 x10-14 | 0.254 x10-9 | 0.834 x10-14 |

Table 5: Results Of Response Spectrum Analysis: 0.6g

| Series | Max. Deflection (mm) | Max. Principle | Max. Von Mises |
| --- | --- | --- | --- |
|  |  | Stress (MPa) | Strain | Stress (MPa) | Strain |
| CT 1 | 9.971 | 0.882172 | 0.284 x10-4 | 0.902337 | 0.285 x10-4 |
| CT 2 | 8.263 | 0.809658 | 0.256 x10-4 | 0.824752 | 0.261 x10-4 |
| CT 3 | 0.167 x10-8 | 0.323 x10-9 | 0986 x10-14 | 0.307 x10-9 | 0.973 x10-14 |

Table 6: Results Of Response Spectrum Analysis: 0.7g

5.4.Wind Analysis

First we creating the Geometry of the model in ANSYS by using key points & we have to input material models, shell element & make mesh to model in Pre processor. By assigning the loads & boundary conditions and input the Pressures along side to the model and solve the problem in solution & read the results in General post processor.

Figure 23: Wind Pressure Applied            Figure 24: Deflection                Figure 25: Principal

Figure 26: Principal Strain                Figure 27: Von Mises Stress         Figure 28: Von Mises Strain

| Series | Max. Deflection (mm) | Max. Principle | Max. Von Mises |
| --- | --- | --- | --- |
|  |  | Stress (MPa) | Strain | Stress (MPa) | Strain |
| CT 1 | 32.715 | 2.015 | 0.640x10-4 | 5.186 | 0.164 x10-3 |
| CT 2 | 23.922 | 1.295 | 0.421 x10-4 | 4.521 | 0.146 x10-3 |
| CT 3 | 57.295 | 2.59 | 0.804 x10-4 | 5.32 | 0.157 x10-3 |

Table 7: Results Of Wind Analysis

6.Conclusion

The main aim of analysis works on CT as follows. In the present study FEA of 3CT viz CT1, CT2, CT3 has been carried out to evaluate principle stress and strain, Von mises stress and strain and deflection.

- CT 1: BTPS cooling tower.

- CT 2: Decrease the Dimensions of cooling tower & Increase the thickness.

- CT 3: Increase the Dimension of cooling tower & Decrease the thickness.

- If dimension is less, deflection is also less and if dimension is more, deflection also more.

- The deflection in static analysis is least for CT2 comparssion to reference tower CT1 and CT3.

- The principal stresses in static analysis i.e (self weight) are observed to be less for CT2 then the reference tower CT1.

- In the free vibration analysis it has been observed that the principal stress for the 1st mode is greater for CT1 than CT2 and CT3.

- It is evident from the seismic analysis. The principal stress observed to be least for CT2 & CT3 comparssion to reference tower CT1.

- It is evident from the seismic analysis that the deflection is the least in CT2 & CT3 compare to reference tower CT1.

- It is evident from the wind load analysis that the deflection is the least in CT2.

- It is evident from the wind load analysis the principal stress is least in CT2 compare to the reference tower CT1and CT3.

7.References

- G. Murali, C. M. Vivek Vardhan and B. V. Prasanth Kumar Reddy, “Response of Cooling Towers To Wind Loads”, ARPN Journal of Engineering and Applied Sciences

- D. Makovička, “Response Analysis of RC cooling tower under seismic and wind storm effect”, Acta Polytechnica Vol. 46 No. 6/2006.

- A. M. El Ansary, A. A. El Damatty, and A. O. Nassef, “Optimum Shape and Design of Cooling Towers”, World Academy of Science, Engineering and Technology 60 2011.

- R.L.Norton, & Weingarten, “The effect of asymmetric imperfections on the earth quake response of hyperbolic cooling towers”,

- Shailesh S. Angalekar, Dr. A. B. Kulkarni, “Analysis of natural draught hyperbolic cooling tower by finite element method using equivalent plate method”,

- IS:11504-1985, “Criteria for structural design of reinforced concrete natural draught cooling tower”, Bureau of Indian standards, New Delhi

- IS:875(Part3)-1987, “Code of practice for design loads (other than earthquake loads) for buildings and structures”, Bureau of Indian Standards, New Delhi

- IS:1893(part 1)- 2002, “Criteria for earthquake resistant design structure”, Bureau of Indian Standards, New Delhi

# Text boxes

Y

X

Abstract:

Natural draught cooling towers are very common in modern day thermal and nuclear power stations. These towers with very small shell thickness are exceptional structures by their shear size and sensitivity to horizontal loads. This paper deals with the Effect of Seismic Load and Wind Loads on Hyperbolic cooling tower of varying dimension and RCC Shell Thickness. For the purpose of comparison an existing cooling tower from one of the power plant is considered. For the other models of cooling towers, the dimensions and thickness of the shell are varied with respect to reference tower. The Boundary conditions considered are; Top end free and Bottom end is fixed. These cooling towers have been analyzed for seismic loads and wind loads using Finite Element Analysis (FEA). The seismic load are carried out for 0.5g, 0.6g and 0.7g in accordance with IS: 1893 (part1)-2002 by modal analysis. Wind loads on these cooling towers have been calculated in the form of pressures by using the design wind pressure coefficients as given in IS: 11504-1985 code along with the design wind pressures at different levels as per IS: 875 (Part 3) - 1987 code. The analysis has been carried out using 8-noded 93 Shell Element. Maximum deflection, maximum principal stress and strains are calculated from the analysis. Maximum Von Mises Stresses and Strains are also calculated.

Key words:  Cooling Tower, FEA, Seismic analysis, Wind analysis, Hyperbolic Shell

Prashanth N

PG Student, Department of Civil Engineering, Ghousia College of Engineering, Ramanagaram

Sayeed Sulaiman

Assistant Professor, Department of Civil Engineering, Ghousia College of Engineering, Ramanagaram

Aswath M U

Professor, Department of Civil Engineering., Bangalore Institute of Technology, Bangalore, India

107.75m

Fig1: Geometry of BTPS

Dthr=61m

Dt=63.6mm

Db=110m

143.5m

35.75m

98.55m

9.2m

107.75m

Dthr=61m

Dt=63.6mm

Db=110m

143.5m

35.75m

98.55m

9.2m

Y

X